## Pipe Dimensions
SMART DOG MININGTM
It takes a smart dog to find hidden treasures
To use enter the required data |  | in the highlighted cells | [5 empty] | William & Hazen Coefficient (C)
To Obtain the Dimensions of a Pipe | [6 empty] | High | Aveage | Low | Design
Enter Nominal Pipe Diameter & Pipe Schedule |  |  |  |  | Cement Lined or Cement |  | 160 | 150 | 140 | 140
Enter Nominal Pipe Diameter, Pipe Schedule, Flow (g.min), & C Factor |  |  |  |  | Fibre |  | 160 | 150 | 140 | 140
[5 empty] | Copper, Brass, glass |  | 150 | 140 | 120 | 130
Nominal Pipe Diameter |  | 2.5 |  |  | Wood stave |  | 145 | 120 | 110 | 110
Pipe Schedule |  | 40 |  |  | Seamless Steel |  | 150 | 140 | 80 | 100
Flow | Q | 92 | g/min |  | Iron |  | 150 | 130 | 80 | 100
C Factor | C | 100 |  |  | Tar Coated |  | 145 | 130 | 80 | 100
Head Loss (ft/100ft) | S | 10.9537 | Feet |  | Concrete |  | 152 | 120 | 85 | 100
Velocity | V | 6.165 | Ft/sec |  | Corrugated Steel |  |  |  | 60 | 60
Velocity Head |  | 0.58911 | Feet
Outside Diameter |  | 2.875 | inches
Wall Thickness |  | 0.203 | inches
Inside diameter | D | 2.469 | inches
Flow Area | A | 4.7878 | inches^2
Weight of Pipe |  | 5.7992 | lb/foot
Weight of Water |  | 2.0755 | lb/foot
Total Weight |  | 7.8747 | lb/foot
WALL THICKNESS
Nominal | Outside | [8 empty] | (inches) | [9 empty] | Nominal | Outside
Diameter | Diameter | 5S | 10S | 10 | LW | 20 | 30 | STD | 40S | 40 | 60 | XS | 80s | 80 | 100 | 120 | 140 | 160 | XXS | Diameter | Diameter
0.125 | 0.405 |  | 0.049 |  |  |  |  | 0.068 | 0.068 | 0.068 |  | 0.095 | 0.095 | 0.095 | [5 empty] | 0.125 | 0.405
0.25 | 0.54 |  | 0.065 |  |  |  |  | 0.088 | 0.088 | 0.088 |  | 0.119 | 0.119 | 0.119 | [5 empty] | 0.25 | 0.54
0.375 | 0.675 |  | 0.065 |  |  |  |  | 0.091 | 0.091 | 0.091 |  | 0.126 | 0.126 | 0.126 | [5 empty] | 0.375 | 0.675
0.5 | 0.84 | 0.065 | 0.083 |  |  |  |  | 0.109 | 0.109 | 0.109 |  | 0.147 | 0.147 | 0.147 |  |  |  | 0.188 | 0.294 | 0.5 | 0.84
0.75 | 1.05 | 0.065 | 0.083 |  |  |  |  | 0.113 | 0.113 | 0.113 |  | 0.154 | 0.154 | 0.154 |  |  |  | 0.219 | 0.308 | 0.75 | 1.05
1 | 1.315 | 0.065 | 0.109 |  |  |  |  | 0.133 | 0.133 | 0.133 |  | 0.179 | 0.179 | 0.179 |  |  |  | 0.25 | 0.358 | 1 | 1.315
1.25 | 1.66 | 0.065 | 0.109 |  |  |  |  | 0.14 | 0.14 | 0.14 |  | 0.191 | 0.191 | 0.191 |  |  |  | 0.25 | 0.382 | 1.25 | 1.66
1.5 | 1.9 | 0.065 | 0.109 |  |  |  |  | 0.145 | 0.145 | 0.145 |  | 0.2 | 0.2 | 0.2 |  |  |  | 0.281 | 0.4 | 1.5 | 1.9
2 | 2.375 | 0.065 | 0.109 |  |  |  |  | 0.154 | 0.154 | 0.154 |  | 0.218 | 0.218 | 0.218 |  |  |  | 0.344 | 0.436 | 2 | 2.375
2.5 | 2.875 | 0.083 | 0.12 |  |  |  |  | 0.203 | 0.203 | 0.203 |  | 0.276 | 0.276 | 0.276 |  |  |  | 0.375 | 0.552 | 2.5 | 2.875
3 | 3.5 | 0.083 | 0.12 |  |  |  |  | 0.216 | 0.216 | 0.216 |  | 0.3 | 0.3 | 0.3 |  |  |  | 0.438 | 0.6 | 3 | 3.5
3.5 | 4 | 0.083 | 0.12 |  |  |  |  | 0.226 | 0.226 | 0.226 |  | 0.318 | 0.318 | 0.318 | [5 empty] | 3.5 | 4
4 | 4.5 | 0.083 | 0.12 |  | 0.188 |  |  | 0.237 | 0.237 | 0.237 |  | 0.337 | 0.337 | 0.337 |  | 0.438 |  | 0.531 | 0.674 | 4 | 4.5
5 | 5.563 | 0.109 | 0.134 |  |  |  |  | 0.258 | 0.258 | 0.258 |  | 0.375 | 0.375 | 0.375 |  | 0.5 |  | 0.625 | 0.75 | 5 | 5.563
6 | 6.625 | 0.109 | 0.134 |  | 0.219 |  |  | 0.28 | 0.28 | 0.28 |  | 0.432 | 0.432 | 0.432 |  | 0.562 |  | 0.719 | 0.864 | 6 | 6.625
8 | 8.625 | 0.109 | 0.138 |  | 0.219 | 0.25 | 0.277 | 0.322 | 0.322 | 0.322 | 0.406 | 0.5 | 0.5 | 0.5 | 0.594 | 0.719 | 0.812 | 0.906 | 0.875 | 8 | 8.625
10 | 10.75 | 0.134 | 0.165 |  | 0.219 | 0.25 | 0.307 | 0.365 | 0.365 | 0.365 | 0.5 | 0.5 | 0.5 | 0.594 | 0.719 | 0.844 | 1 | 1.125 | 1 | 10 | 10.75
12 | 12.75 | 0.156 | 0.18 |  | 0.25 | 0.25 | 0.33 | 0.375 | 0.375 | 0.406 | 0.562 | 0.5 | 0.5 | 0.688 | 0.844 | 1 | 1.125 | 1.312 | 1 | 12 | 12.75
14 | 14 | 0.156 | 0.188 | 0.25 | 0.25 | 0.312 | 0.375 | 0.375 |  | 0.438 | 0.594 | 0.5 |  | 0.75 | 0.938 | 1.094 | 1.25 | 1.406 |  | 14 | 14
16 | 16 | 0.165 | 0.188 | 0.25 | 0.25 | 0.312 | 0.375 | 0.375 |  | 0.5 | 0.656 | 0.5 |  | 0.844 | 1.031 | 1.219 | 1.438 | 1.594 |  | 16 | 16
18 | 18 | 0.165 | 0.188 | 0.25 | 0.25 | 0.312 | 0.438 | 0.375 |  | 0.562 | 0.75 | 0.5 |  | 0.938 | 1.156 | 1.375 | 1.562 | 1.781 |  | 18 | 18
20 | 20 | 0.188 | 0.218 | 0.25 | 0.25 | 0.375 | 0.5 | 0.375 |  | 0.594 | 0.812 | 0.5 |  | 1.031 | 1.281 | 1.5 | 1.75 | 1.969 |  | 20 | 20
22 | 22 | 0.188 | 0.218 | 0.25 | 0.25 | 0.375 | 0.5 | 0.375 |  |  | 0.875 | 0.5 |  | 1.125 | 1.375 | 1.625 | 1.875 | 2.125 |  | 22 | 22
24 | 24 | 0.218 | 0.25 | 0.25 | 0.25 | 0.375 | 0.562 | 0.375 |  | 0.688 | 0.969 | 0.5 |  | 1.218 | 1.531 | 1.812 | 2.062 | 2.344 |  | 24 | 24
26 | 26 |  |  | 0.312 |  | 0.5 |  | 0.375 |  |  |  | 0.5 | [7 empty] | 26 | 26
28 | 28 |  |  | 0.312 |  | 0.5 | 0.625 | 0.375 |  |  |  | 0.5 | [7 empty] | 28 | 28
30 | 30 | 0.25 | 0.312 | 0.312 |  | 0.5 | 0.625 | 0.375 |  |  |  | 0.5 | [7 empty] | 30 | 30
32 | 32 |  |  | 0.312 |  | 0.5 | 0.625 | 0.375 |  | 0.688 |  | 0.5 | [7 empty] | 32 | 32
34 | 34 |  |  | 0.312 |  | 0.5 | 0.625 | 0.375 |  | 0.688 |  | 0.5 | [7 empty] | 34 | 34
36 | 36 |  |  | 0.312 |  | 0.5 | 0.625 | 0.375 |  | 0.75 |  | 0.5 | [7 empty] | 36 | 36
42 | 42 | [6 empty] | 0.375 |  |  |  | 0.5 | [7 empty] | 42 | 42
INSIDE DIAMETER
Nominal | Outside | [8 empty] | (inches) | [9 empty] | Nominal | Outside
Diameter | Diameter | 5S | 10S | 10 | LW | 20 | 30 | STD | 40S | 40 | 60 | XS | 80s | 80 | 100 | 120 | 140 | 160 | XXS | Diameter | Diameter
0.125 | 0.405 | 0 | 0.307 | 0 | 0 | 0 | 0 | 0.269 | 0.269 | 0.269 | 0 | 0.215 | 0.215 | 0.215 | 0 | 0 | 0 | 0 | 0 | 0.125 | 0.405
0.25 | 0.54 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0.364 | 0.364 | 0.364 | 0 | 0.302 | 0.302 | 0.302 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.54
0.375 | 0.675 | 0 | 0.545 | 0 | 0 | 0 | 0 | 0.493 | 0.493 | 0.493 | 0 | 0.423 | 0.423 | 0.423 | 0 | 0 | 0 | 0 | 0 | 0.375 | 0.675
0.5 | 0.84 | 0.71 | 0.674 | 0 | 0 | 0 | 0 | 0.622 | 0.622 | 0.622 | 0 | 0.546 | 0.546 | 0.546 | 0 | 0 | 0 | 0.464 | 0.252 | 0.5 | 0.84
0.75 | 1.05 | 0.92 | 0.884 | 0 | 0 | 0 | 0 | 0.824 | 0.824 | 0.824 | 0 | 0.742 | 0.742 | 0.742 | 0 | 0 | 0 | 0.612 | 0.434 | 0.75 | 1.05
1 | 1.315 | 1.185 | 1.097 | 0 | 0 | 0 | 0 | 1.049 | 1.049 | 1.049 | 0 | 0.957 | 0.957 | 0.957 | 0 | 0 | 0 | 0.815 | 0.599 | 1 | 1.315
1.25 | 1.66 | 1.53 | 1.442 | 0 | 0 | 0 | 0 | 1.38 | 1.38 | 1.38 | 0 | 1.278 | 1.278 | 1.278 | 0 | 0 | 0 | 1.16 | 0.896 | 1.25 | 1.66
1.5 | 1.9 | 1.77 | 1.682 | 0 | 0 | 0 | 0 | 1.61 | 1.61 | 1.61 | 0 | 1.5 | 1.5 | 1.5 | 0 | 0 | 0 | 1.338 | 1.1 | 1.5 | 1.9
2 | 2.375 | 2.245 | 2.157 | 0 | 0 | 0 | 0 | 2.067 | 2.067 | 2.067 | 0 | 1.939 | 1.939 | 1.939 | 0 | 0 | 0 | 1.687 | 1.503 | 2 | 2.375
2.5 | 2.875 | 2.709 | 2.635 | 0 | 0 | 0 | 0 | 2.469 | 2.469 | 2.469 | 0 | 2.323 | 2.323 | 2.323 | 0 | 0 | 0 | 2.125 | 1.771 | 2.5 | 2.875
3 | 3.5 | 3.334 | 3.26 | 0 | 0 | 0 | 0 | 3.068 | 3.068 | 3.068 | 0 | 2.9 | 2.9 | 2.9 | 0 | 0 | 0 | 2.624 | 2.3 | 3 | 3.5
3.5 | 4 | 3.834 | 3.76 | 0 | 0 | 0 | 0 | 3.548 | 3.548 | 3.548 | 0 | 3.364 | 3.364 | 3.364 | 0 | 0 | 0 | 0 | 0 | 3.5 | 4
4 | 4.5 | 4.334 | 4.26 | 0 | 4.124 | 0 | 0 | 4.026 | 4.026 | 4.026 | 0 | 3.826 | 3.826 | 3.826 | 0 | 3.624 | 0 | 3.438 | 3.152 | 4 | 4.5
5 | 5.563 | 5.345 | 5.295 | 0 | 0 | 0 | 0 | 5.047 | 5.047 | 5.047 | 0 | 4.813 | 4.813 | 4.813 | 0 | 4.563 | 0 | 4.313 | 4.063 | 5 | 5.563
6 | 6.625 | 6.407 | 6.357 | 0 | 6.187 | 0 | 0 | 6.065 | 6.065 | 6.065 | 0 | 5.761 | 5.761 | 5.761 | 0 | 5.501 | 0 | 5.187 | 4.897 | 6 | 6.625
8 | 8.625 | 8.407 | 8.349 | 0 | 8.187 | 8.125 | 8.071 | 7.981 | 7.981 | 7.981 | 7.813 | 7.625 | 7.625 | 7.625 | 7.437 | 7.187 | 7.001 | 6.813 | 6.875 | 8 | 8.625
10 | 10.75 | 10.482 | 10.42 | 0 | 10.312 | 10.25 | 10.136 | 10.02 | 10.02 | 10.02 | 9.75 | 9.75 | 9.75 | 9.562 | 9.312 | 9.062 | 8.75 | 8.5 | 8.75 | 10 | 10.75
12 | 12.75 | 12.438 | 12.39 | 0 | 12.25 | 12.25 | 12.09 | 12 | 12 | 11.938 | 11.626 | 11.75 | 11.75 | 11.374 | 11.062 | 10.75 | 10.5 | 10.126 | 10.75 | 12 | 12.75
14 | 14 | 13.688 | 13.624 | 13.5 | 13.5 | 13.376 | 13.25 | 13.25 | 0 | 13.124 | 12.812 | 13 | 0 | 12.5 | 12.124 | 11.812 | 11.5 | 11.188 | 0 | 14 | 14
16 | 16 | 15.67 | 15.624 | 15.5 | 15.5 | 15.376 | 15.25 | 15.25 | 0 | 15 | 14.688 | 15 | 0 | 14.312 | 13.938 | 13.562 | 13.124 | 12.812 | 0 | 16 | 16
18 | 18 | 17.67 | 17.624 | 17.5 | 17.5 | 17.376 | 17.124 | 17.25 | 0 | 16.876 | 16.5 | 17 | 0 | 16.124 | 15.688 | 15.25 | 14.876 | 14.438 | 0 | 18 | 18
20 | 20 | 19.624 | 19.564 | 19.5 | 19.5 | 19.25 | 19 | 19.25 | 0 | 18.812 | 18.376 | 19 | 0 | 17.938 | 17.438 | 17 | 16.5 | 16.062 | 0 | 20 | 20
22 | 22 | 21.624 | 21.564 | 21.5 | 21.5 | 21.25 | 21 | 21.25 | 0 | 0 | 20.25 | 21 | 0 | 19.75 | 19.25 | 18.75 | 18.25 | 17.75 | 0 | 22 | 22
24 | 24 | 23.564 | 23.5 | 23.5 | 23.5 | 23.25 | 22.876 | 23.25 | 0 | 22.624 | 22.062 | 23 | 0 | 21.564 | 20.938 | 20.376 | 19.876 | 19.312 | 0 | 24 | 24
26 | 26 | 0 | 0 | 25.376 | 0 | 25 | 0 | 25.25 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26
28 | 28 | 0 | 0 | 27.376 | 0 | 27 | 26.75 | 27.25 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 28
30 | 30 | 29.5 | 29.376 | 29.376 | 0 | 29 | 28.75 | 29.25 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30
32 | 32 | 0 | 0 | 31.376 | 0 | 31 | 30.75 | 31.25 | 0 | 30.624 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32
34 | 34 | 0 | 0 | 33.376 | 0 | 33 | 32.75 | 33.25 | 0 | 32.624 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
36 | 36 | 0 | 0 | 35.376 | 0 | 35 | 34.75 | 35.25 | 0 | 34.5 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 41.25 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 42
FLOW AREA
Nominal | Outside | [8 empty] | (square inches) | [9 empty] | Nominal | Outside
Diameter | Diameter | 5S | 10S | 10 | LW | 20 | 30 | STD | 40S | 40 | 60 | XS | 80s | 80 | 100 | 120 | 140 | 160 | XXS | Diameter | Diameter
0.125 | 0.405 | 0 | 0.074023 | 0 | 0 | 0 | 0 | 0.056832 | 0.056832 | 0.056832 | 0 | 0.036305 | 0.036305 | 0.036305 | 0 | 0 | 0 | 0 | 0 | 0.125 | 0.405
0.25 | 0.54 | 0 | 0.13203 | 0 | 0 | 0 | 0 | 0.10406 | 0.10406 | 0.10406 | 0 | 0.071631 | 0.071631 | 0.071631 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.54
0.375 | 0.675 | 0 | 0.23328 | 0 | 0 | 0 | 0 | 0.19089 | 0.19089 | 0.19089 | 0 | 0.14053 | 0.14053 | 0.14053 | 0 | 0 | 0 | 0 | 0 | 0.375 | 0.675
0.5 | 0.84 | 0.39592 | 0.35679 | 0 | 0 | 0 | 0 | 0.30386 | 0.30386 | 0.30386 | 0 | 0.23414 | 0.23414 | 0.23414 | 0 | 0 | 0 | 0.16909 | 0.049876 | 0.5 | 0.84
0.75 | 1.05 | 0.66476 | 0.61375 | 0 | 0 | 0 | 0 | 0.53327 | 0.53327 | 0.53327 | 0 | 0.43241 | 0.43241 | 0.43241 | 0 | 0 | 0 | 0.29417 | 0.14793 | 0.75 | 1.05
1 | 1.315 | 1.1029 | 0.94516 | 0 | 0 | 0 | 0 | 0.86425 | 0.86425 | 0.86425 | 0 | 0.71931 | 0.71931 | 0.71931 | 0 | 0 | 0 | 0.52168 | 0.2818 | 1 | 1.315
1.25 | 1.66 | 1.8385 | 1.6331 | 0 | 0 | 0 | 0 | 1.4957 | 1.4957 | 1.4957 | 0 | 1.2828 | 1.2828 | 1.2828 | 0 | 0 | 0 | 1.0568 | 0.63053 | 1.25 | 1.66
1.5 | 1.9 | 2.4606 | 2.222 | 0 | 0 | 0 | 0 | 2.0358 | 2.0358 | 2.0358 | 0 | 1.7671 | 1.7671 | 1.7671 | 0 | 0 | 0 | 1.4061 | 0.95033 | 1.5 | 1.9
2 | 2.375 | 3.9584 | 3.6542 | 0 | 0 | 0 | 0 | 3.3556 | 3.3556 | 3.3556 | 0 | 2.9529 | 2.9529 | 2.9529 | 0 | 0 | 0 | 2.2352 | 1.7742 | 2 | 2.375
2.5 | 2.875 | 5.7638 | 5.4532 | 0 | 0 | 0 | 0 | 4.7878 | 4.7878 | 4.7878 | 0 | 4.2383 | 4.2383 | 4.2383 | 0 | 0 | 0 | 3.5466 | 2.4634 | 2.5 | 2.875
3 | 3.5 | 8.7301 | 8.3469 | 0 | 0 | 0 | 0 | 7.3927 | 7.3927 | 7.3927 | 0 | 6.6052 | 6.6052 | 6.6052 | 0 | 0 | 0 | 5.4078 | 4.1548 | 3 | 3.5
3.5 | 4 | 11.545 | 11.1036 | 0 | 0 | 0 | 0 | 9.8868 | 9.8868 | 9.8868 | 0 | 8.888 | 8.888 | 8.888 | 0 | 0 | 0 | 0 | 0 | 3.5 | 4
4 | 4.5 | 14.7526 | 14.2531 | 0 | 13.3576 | 0 | 0 | 12.7303 | 12.7303 | 12.7303 | 0 | 11.4969 | 11.4969 | 11.4969 | 0 | 10.3149 | 0 | 9.2833 | 7.803 | 4 | 4.5
5 | 5.563 | 22.4381 | 22.0202 | 0 | 0 | 0 | 0 | 20.0058 | 20.0058 | 20.0058 | 0 | 18.1937 | 18.1937 | 18.1937 | 0 | 16.3528 | 0 | 14.61 | 12.9653 | 5 | 5.563
6 | 6.625 | 32.2403 | 31.7391 | 0 | 30.0642 | 0 | 0 | 28.8903 | 28.8903 | 28.8903 | 0 | 26.0667 | 26.0667 | 26.0667 | 0 | 23.7669 | 0 | 21.1311 | 18.8343 | 6 | 6.625
8 | 8.625 | 55.5101 | 54.7468 | 0 | 52.6429 | 51.8486 | 51.1617 | 50.027 | 50.027 | 50.027 | 47.943 | 45.6635 | 45.6635 | 45.6635 | 43.4396 | 40.5681 | 38.4955 | 36.4558 | 37.1223 | 8 | 8.625
10 | 10.75 | 86.2935 | 85.2757 | 0 | 83.5172 | 82.5159 | 80.6906 | 78.8543 | 78.8543 | 78.8543 | 74.6619 | 74.6619 | 74.6619 | 71.8104 | 68.1045 | 64.4968 | 60.132 | 56.745 | 60.132 | 10 | 10.75
12 | 12.75 | 121.5041 | 120.5681 | 0 | 117.8588 | 117.8588 | 114.8002 | 113.0973 | 113.0973 | 111.9317 | 106.1575 | 108.434 | 108.434 | 101.6053 | 96.1075 | 90.7626 | 86.5901 | 80.5315 | 90.7626 | 12 | 12.75
14 | 14 | 147.1533 | 145.7804 | 143.1388 | 143.1388 | 140.5214 | 137.8865 | 137.8865 | 0 | 135.2765 | 128.921 | 132.7323 | 0 | 122.7185 | 115.4468 | 109.5814 | 103.8689 | 98.3093 | 0 | 14 | 14
16 | 16 | 192.8537 | 191.7231 | 188.6919 | 188.6919 | 185.6849 | 182.6542 | 182.6542 | 0 | 176.7146 | 169.4397 | 176.7146 | 0 | 160.8757 | 152.5776 | 144.4566 | 135.2765 | 128.921 | 0 | 16 | 16
18 | 18 | 245.224 | 243.9489 | 240.5282 | 240.5282 | 237.1316 | 230.3034 | 233.705 | 0 | 223.6809 | 213.8246 | 226.9801 | 0 | 204.1905 | 193.297 | 182.6542 | 173.805 | 163.7208 | 0 | 18 | 18
20 | 20 | 302.4579 | 300.6112 | 298.6477 | 298.6477 | 291.0391 | 283.5287 | 291.0391 | 0 | 277.9456 | 265.2112 | 283.5287 | 0 | 252.719 | 238.8269 | 226.9801 | 213.8246 | 202.6232 | 0 | 20 | 20
22 | 22 | 367.2501 | 365.2149 | 363.0503 | 363.0503 | 354.6564 | 346.3606 | 354.6564 | 0 | 0 | 322.0623 | 346.3606 | 0 | 306.3544 | 291.0391 | 276.1165 | 261.5867 | 247.4495 | 0 | 22 | 22
24 | 24 | 436.1018 | 433.7361 | 433.7361 | 433.7361 | 424.5568 | 411.0078 | 424.5568 | 0 | 402.0024 | 382.2783 | 415.4756 | 0 | 365.2149 | 344.3184 | 326.0827 | 310.2758 | 292.9169 | 0 | 24 | 24
26 | 26 | 0 | 0 | 505.7504 | 0 | 490.8739 | 0 | 500.7404 | 0 | 0 | 0 | 490.8739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26
28 | 28 | 0 | 0 | 588.613 | 0 | 572.5553 | 562.0015 | 583.2072 | 0 | 0 | 0 | 572.5553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 28
30 | 30 | 683.4928 | 677.7589 | 677.7589 | 0 | 660.5199 | 649.1807 | 671.9572 | 0 | 0 | 0 | 660.5199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30
32 | 32 | 0 | 0 | 773.1879 | 0 | 754.7676 | 742.6431 | 766.9904 | 0 | 736.5695 | 0 | 754.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32
34 | 34 | 0 | 0 | 874.9001 | 0 | 855.2986 | 842.3886 | 868.3068 | 0 | 835.9192 | 0 | 855.2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
36 | 36 | 0 | 0 | 982.8955 | 0 | 962.1128 | 948.4174 | 975.9063 | 0 | 934.8202 | 0 | 962.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 1336.4041 | 0 | 0 | 0 | 1320.2543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 42
AREA OF METAL
Nominal | Outside | [8 empty] | (square inches) | [9 empty] | Nominal | Outside
Diameter | Diameter | 5S | 10S | 10 | LW | 20 | 30 | STD | 40S | 40 | 60 | XS | 80s | 80 | 100 | 120 | 140 | 160 | XXS | Diameter | Diameter
0.125 | 0.405 | 0 | 0.054802 | 0 | 0 | 0 | 0 | 0.071993 | 0.071993 | 0.071993 | 0 | 0.09252 | 0.09252 | 0.09252 | 0 | 0 | 0 | 0 | 0 | 0.125 | 0.405
0.25 | 0.54 | 0 | 0.096997 | 0 | 0 | 0 | 0 | 0.12496 | 0.12496 | 0.12496 | 0 | 0.15739 | 0.15739 | 0.15739 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.54
0.375 | 0.675 | 0 | 0.12456 | 0 | 0 | 0 | 0 | 0.16696 | 0.16696 | 0.16696 | 0 | 0.21732 | 0.21732 | 0.21732 | 0 | 0 | 0 | 0 | 0 | 0.375 | 0.675
0.5 | 0.84 | 0.15826 | 0.19739 | 0 | 0 | 0 | 0 | 0.25032 | 0.25032 | 0.25032 | 0 | 0.32004 | 0.32004 | 0.32004 | 0 | 0 | 0 | 0.38508 | 0.5043 | 0.5 | 0.84
0.75 | 1.05 | 0.20114 | 0.25215 | 0 | 0 | 0 | 0 | 0.33263 | 0.33263 | 0.33263 | 0 | 0.43349 | 0.43349 | 0.43349 | 0 | 0 | 0 | 0.57174 | 0.71797 | 0.75 | 1.05
1 | 1.315 | 0.25525 | 0.41297 | 0 | 0 | 0 | 0 | 0.49388 | 0.49388 | 0.49388 | 0 | 0.63882 | 0.63882 | 0.63882 | 0 | 0 | 0 | 0.83645 | 1.0763 | 1 | 1.315
1.25 | 1.66 | 0.3257 | 0.53111 | 0 | 0 | 0 | 0 | 0.66853 | 0.66853 | 0.66853 | 0 | 0.88146 | 0.88146 | 0.88146 | 0 | 0 | 0 | 1.1074 | 1.5337 | 1.25 | 1.66
1.5 | 1.9 | 0.37471 | 0.6133 | 0 | 0 | 0 | 0 | 0.79946 | 0.79946 | 0.79946 | 0 | 1.0681 | 1.0681 | 1.0681 | 0 | 0 | 0 | 1.4292 | 1.885 | 1.5 | 1.9
2 | 2.375 | 0.47171 | 0.77595 | 0 | 0 | 0 | 0 | 1.0745 | 1.0745 | 1.0745 | 0 | 1.4773 | 1.4773 | 1.4773 | 0 | 0 | 0 | 2.1949 | 2.6559 | 2 | 2.375
2.5 | 2.875 | 0.72802 | 1.0386 | 0 | 0 | 0 | 0 | 1.7041 | 1.7041 | 1.7041 | 0 | 2.2535 | 2.2535 | 2.2535 | 0 | 0 | 0 | 2.9452 | 4.0285 | 2.5 | 2.875
3 | 3.5 | 0.89099 | 1.2742 | 0 | 0 | 0 | 0 | 2.2285 | 2.2285 | 2.2285 | 0 | 3.0159 | 3.0159 | 3.0159 | 0 | 0 | 0 | 4.2134 | 5.4664 | 3 | 3.5
3.5 | 4 | 1.0214 | 1.4627 | 0 | 0 | 0 | 0 | 2.6795 | 2.6795 | 2.6795 | 0 | 3.6784 | 3.6784 | 3.6784 | 0 | 0 | 0 | 0 | 0 | 3.5 | 4
4 | 4.5 | 1.1517 | 1.6512 | 0 | 2.5468 | 0 | 0 | 3.174 | 3.174 | 3.174 | 0 | 4.4074 | 4.4074 | 4.4074 | 0 | 5.5894 | 0 | 6.621 | 8.1013 | 4 | 4.5
5 | 5.563 | 1.8676 | 2.2855 | 0 | 0 | 0 | 0 | 4.2999 | 4.2999 | 4.2999 | 0 | 6.112 | 6.112 | 6.112 | 0 | 7.9529 | 0 | 9.6957 | 11.3404 | 5 | 5.563
6 | 6.625 | 2.2313 | 2.7325 | 0 | 4.4074 | 0 | 0 | 5.5814 | 5.5814 | 5.5814 | 0 | 8.4049 | 8.4049 | 8.4049 | 0 | 10.7047 | 0 | 13.3405 | 15.6373 | 6 | 6.625
8 | 8.625 | 2.9162 | 3.6795 | 0 | 5.7834 | 6.5777 | 7.2646 | 8.3993 | 8.3993 | 8.3993 | 10.4832 | 12.7627 | 12.7627 | 12.7627 | 14.9867 | 17.8581 | 19.9308 | 21.9705 | 21.3039 | 8 | 8.625
10 | 10.75 | 4.4691 | 5.4869 | 0 | 7.2454 | 8.2467 | 10.0719 | 11.9083 | 11.9083 | 11.9083 | 16.1007 | 16.1007 | 16.1007 | 18.9522 | 22.6581 | 26.2658 | 30.6305 | 34.0176 | 30.6305 | 10 | 10.75
12 | 12.75 | 6.1722 | 7.1082 | 0 | 9.8175 | 9.8175 | 12.8761 | 14.579 | 14.579 | 15.7446 | 21.5188 | 19.2423 | 19.2423 | 26.071 | 31.5688 | 36.9137 | 41.0861 | 47.1448 | 36.9137 | 12 | 12.75
14 | 14 | 6.7848 | 8.1576 | 10.7992 | 10.7992 | 13.4167 | 16.0516 | 16.0516 | 0 | 18.6616 | 25.017 | 21.2058 | 0 | 31.2196 | 38.4913 | 44.3567 | 50.0691 | 55.6287 | 0 | 14 | 14
16 | 16 | 8.2083 | 9.3389 | 12.37 | 12.37 | 15.377 | 18.4078 | 18.4078 | 0 | 24.3473 | 31.6222 | 24.3473 | 0 | 40.1862 | 48.4843 | 56.6053 | 65.7854 | 72.1409 | 0 | 16 | 16
18 | 18 | 9.245 | 10.5201 | 13.9408 | 13.9408 | 17.3374 | 24.1656 | 20.764 | 0 | 30.7881 | 40.6444 | 27.4889 | 0 | 50.2785 | 61.172 | 71.8148 | 80.664 | 90.7482 | 0 | 18 | 18
20 | 20 | 11.7014 | 13.548 | 15.5116 | 15.5116 | 23.1202 | 30.6305 | 23.1202 | 0 | 36.2137 | 48.9481 | 30.6305 | 0 | 61.4403 | 75.3324 | 87.1792 | 100.3346 | 111.5361 | 0 | 20 | 20
22 | 22 | 12.8826 | 14.9178 | 17.0824 | 17.0824 | 25.4764 | 33.7721 | 25.4764 | 0 | 0 | 58.0704 | 33.7721 | 0 | 73.7783 | 89.0936 | 104.0162 | 118.546 | 132.6832 | 0 | 22 | 22
24 | 24 | 16.2875 | 18.6532 | 18.6532 | 18.6532 | 27.8325 | 41.3815 | 27.8325 | 0 | 50.3869 | 70.111 | 36.9137 | 0 | 87.1744 | 108.0709 | 126.3067 | 142.1136 | 159.4725 | 0 | 24 | 24
26 | 26 | 0 | 0 | 25.1788 | 0 | 40.0553 | 0 | 30.1887 | 0 | 0 | 0 | 40.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26
28 | 28 | 0 | 0 | 27.1391 | 0 | 43.1969 | 53.7507 | 32.5449 | 0 | 0 | 0 | 43.1969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 28
30 | 30 | 23.3656 | 29.0995 | 29.0995 | 0 | 46.3385 | 57.6777 | 34.9011 | 0 | 0 | 0 | 46.3385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30
32 | 32 | 0 | 0 | 31.0598 | 0 | 49.4801 | 61.6047 | 37.2573 | 0 | 67.6782 | 0 | 49.4801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32
34 | 34 | 0 | 0 | 33.0202 | 0 | 52.6217 | 65.5317 | 39.6135 | 0 | 72.0011 | 0 | 52.6217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
36 | 36 | 0 | 0 | 34.9806 | 0 | 55.7633 | 69.4587 | 41.9697 | 0 | 83.0559 | 0 | 55.7633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 49.0383 | 0 | 0 | 0 | 65.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 42
ss = | 0.28644 | lbs/in^3 | 494.3885 | lbs/ft^3
cs = | 0.2836 | lbs/in^3 | 489.4936 | lbs/ft^3 | [5 empty] | WEIGHT OF PIPE
Nominal | Outside | [8 empty] | (pounds/foot | [9 empty] | Nominal | Outside
Diameter | Diameter | 5S | 10S | 10 | LW | 20 | 30 | STD | 40S | 40 | 60 | XS | 80s | 80 | 100 | 120 | 140 | 160 | XXS | Diameter | Diameter
0.125 | 0.405 | 0 | 0.18837 | 0 | 0 | 0 | 0 | 0.24501 | 0.24746 | 0.24501 | 0 | 0.31486 | 0.31801 | 0.31486 | 0 | 0 | 0 | 0 | 0 | 0.125 | 0.405
0.25 | 0.54 | 0 | 0.3334 | 0 | 0 | 0 | 0 | 0.42526 | 0.42952 | 0.42526 | 0 | 0.53563 | 0.54099 | 0.53563 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.54
0.375 | 0.675 | 0 | 0.42816 | 0 | 0 | 0 | 0 | 0.56819 | 0.57387 | 0.56819 | 0 | 0.73957 | 0.74697 | 0.73957 | 0 | 0 | 0 | 0 | 0 | 0.375 | 0.675
0.5 | 0.84 | 0.54397 | 0.67847 | 0 | 0 | 0 | 0 | 0.85189 | 0.8604 | 0.85189 | 0 | 1.0892 | 1.1 | 1.0892 | 0 | 0 | 0 | 1.3105 | 1.7162 | 0.5 | 0.84
0.75 | 1.05 | 0.69137 | 0.86669 | 0 | 0 | 0 | 0 | 1.132 | 1.1433 | 1.132 | 0 | 1.4753 | 1.49 | 1.4753 | 0 | 0 | 0 | 1.9457 | 2.4434 | 0.75 | 1.05
1 | 1.315 | 0.87737 | 1.4195 | 0 | 0 | 0 | 0 | 1.6808 | 1.6976 | 1.6808 | 0 | 2.174 | 2.1958 | 2.174 | 0 | 0 | 0 | 2.8466 | 3.663 | 1 | 1.315
1.25 | 1.66 | 1.1195 | 1.8256 | 0 | 0 | 0 | 0 | 2.2751 | 2.2979 | 2.2751 | 0 | 2.9998 | 3.0298 | 2.9998 | 0 | 0 | 0 | 3.7687 | 5.2195 | 1.25 | 1.66
1.5 | 1.9 | 1.288 | 2.108 | 0 | 0 | 0 | 0 | 2.7207 | 2.7479 | 2.7207 | 0 | 3.6351 | 3.6715 | 3.6351 | 0 | 0 | 0 | 4.864 | 6.4149 | 1.5 | 1.9
2 | 2.375 | 1.6214 | 2.6671 | 0 | 0 | 0 | 0 | 3.6568 | 3.6934 | 3.6568 | 0 | 5.0274 | 5.0777 | 5.0274 | 0 | 0 | 0 | 7.4697 | 9.0386 | 2 | 2.375
2.5 | 2.875 | 2.5024 | 3.5699 | 0 | 0 | 0 | 0 | 5.7992 | 5.8572 | 5.7992 | 0 | 7.6692 | 7.7459 | 7.6692 | 0 | 0 | 0 | 10.0233 | 13.7096 | 2.5 | 2.875
3 | 3.5 | 3.0625 | 4.3798 | 0 | 0 | 0 | 0 | 7.5839 | 7.6598 | 7.5839 | 0 | 10.2638 | 10.3664 | 10.2638 | 0 | 0 | 0 | 14.3389 | 18.6032 | 3 | 3.5
3.5 | 4 | 3.5107 | 5.0277 | 0 | 0 | 0 | 0 | 9.119 | 9.2102 | 9.119 | 0 | 12.5184 | 12.6436 | 12.5184 | 0 | 0 | 0 | 0 | 0 | 3.5 | 4
4 | 4.5 | 3.9588 | 5.6756 | 0 | 8.6671 | 0 | 0 | 10.8019 | 10.9099 | 10.8019 | 0 | 14.9994 | 15.1494 | 14.9994 | 0 | 19.0218 | 0 | 22.5327 | 27.5703 | 4 | 4.5
5 | 5.563 | 6.4195 | 7.8557 | 0 | 0 | 0 | 0 | 14.6333 | 14.7796 | 14.6333 | 0 | 20.8003 | 21.0083 | 20.8003 | 0 | 27.0655 | 0 | 32.9965 | 38.5935 | 5 | 5.563
6 | 6.625 | 7.6695 | 9.3924 | 0 | 14.9992 | 0 | 0 | 18.9945 | 19.1844 | 18.9945 | 0 | 28.6037 | 28.8897 | 28.6037 | 0 | 36.4302 | 0 | 45.4004 | 53.2168 | 6 | 6.625
8 | 8.625 | 10.0235 | 12.6471 | 0 | 19.6821 | 22.3853 | 24.7229 | 28.5843 | 28.8702 | 28.5843 | 35.6765 | 43.4341 | 43.8684 | 43.4341 | 51.0027 | 60.7747 | 67.8283 | 74.7699 | 72.5015 | 8 | 8.625
10 | 10.75 | 15.3612 | 18.8596 | 0 | 24.6576 | 28.0651 | 34.2769 | 40.5263 | 40.9315 | 40.5263 | 54.7938 | 54.7938 | 55.3417 | 64.498 | 77.11 | 89.3878 | 104.2418 | 115.7686 | 104.2418 | 10 | 10.75
12 | 12.75 | 21.2152 | 24.4324 | 0 | 33.4108 | 33.4108 | 43.8201 | 49.6151 | 50.1112 | 53.582 | 73.2329 | 65.4852 | 66.1401 | 88.7248 | 107.435 | 125.6248 | 139.8244 | 160.4432 | 125.6248 | 12 | 12.75
14 | 14 | 23.3209 | 28.0397 | 36.7519 | 36.7519 | 45.6596 | 54.6267 | 54.6267 | 0 | 63.509 | 85.1379 | 72.1674 | 0 | 106.2465 | 130.9935 | 150.9546 | 170.3953 | 189.3156 | 0 | 14 | 14
16 | 16 | 28.2137 | 32.0999 | 42.0977 | 42.0977 | 52.3311 | 62.6453 | 62.6453 | 0 | 82.8589 | 107.6167 | 82.8589 | 0 | 136.7617 | 165.0018 | 192.6393 | 223.881 | 245.5099 | 0 | 16 | 16
18 | 18 | 31.7772 | 36.1601 | 47.4434 | 47.4434 | 59.0025 | 82.2404 | 70.6639 | 0 | 104.7781 | 138.3209 | 93.5503 | 0 | 171.1079 | 208.1807 | 244.4003 | 274.5158 | 308.8342 | 0 | 18 | 18
20 | 20 | 40.2203 | 46.5678 | 52.7891 | 52.7891 | 78.6825 | 104.2418 | 78.6825 | 0 | 123.2423 | 166.5801 | 104.2418 | 0 | 209.0935 | 256.3711 | 296.6882 | 341.4588 | 379.5796 | 0 | 20 | 20
22 | 22 | 44.2805 | 51.2759 | 58.1349 | 58.1349 | 86.7011 | 114.9333 | 86.7011 | 0 | 0 | 197.6251 | 114.9333 | 0 | 251.0824 | 303.2034 | 353.9878 | 403.4359 | 451.5475 | 0 | 22 | 22
24 | 24 | 55.984 | 64.1154 | 63.4806 | 63.4806 | 94.7197 | 140.8297 | 94.7197 | 0 | 171.4768 | 238.6019 | 125.6248 | 0 | 296.6719 | 367.7869 | 429.8468 | 483.6409 | 542.7167 | 0 | 24 | 24
26 | 26 | 0 | 0 | 85.6884 | 0 | 136.3162 | 0 | 102.7383 | 0 | 0 | 0 | 136.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26
28 | 28 | 0 | 0 | 92.3599 | 0 | 147.0077 | 182.9243 | 110.7569 | 0 | 0 | 0 | 147.0077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 28
30 | 30 | 80.313 | 100.0217 | 99.0314 | 0 | 157.6992 | 196.2887 | 118.7755 | 0 | 0 | 0 | 157.6992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30
32 | 32 | 0 | 0 | 105.7029 | 0 | 168.3906 | 209.653 | 126.7941 | 0 | 230.3226 | 0 | 168.3906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32
34 | 34 | 0 | 0 | 112.3743 | 0 | 179.0821 | 223.0173 | 134.8127 | 0 | 245.0341 | 0 | 179.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
36 | 36 | 0 | 0 | 119.0458 | 0 | 189.7736 | 236.3817 | 142.8313 | 0 | 282.6557 | 0 | 189.7736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 166.8871 | 0 | 0 | 0 | 221.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 42
Water | 62.425 | lbs/ft^3 | [7 empty] | WEIGHT OF WATER
Nominal | Outside | [8 empty] | (pounds/foot) | [9 empty] | Nominal | Outside
Diameter | Diameter | 5S | 10S | 10 | LW | 20 | 30 | STD | 40S | 40 | 60 | XS | 80s | 80 | 100 | 120 | 140 | 160 | XXS | Diameter | Diameter
0.125 | 0.405 | 0 | 0.032089 | 0 | 0 | 0 | 0 | 0.024637 | 0.024637 | 0.024637 | 0 | 0.015738 | 0.015738 | 0.015738 | 0 | 0 | 0 | 0 | 0 | 0.125 | 0.405
0.25 | 0.54 | 0 | 0.057234 | 0 | 0 | 0 | 0 | 0.045112 | 0.045112 | 0.045112 | 0 | 0.031053 | 0.031053 | 0.031053 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.54
0.375 | 0.675 | 0 | 0.10113 | 0 | 0 | 0 | 0 | 0.082752 | 0.082752 | 0.082752 | 0 | 0.060921 | 0.060921 | 0.060921 | 0 | 0 | 0 | 0 | 0 | 0.375 | 0.675
0.5 | 0.84 | 0.17163 | 0.15467 | 0 | 0 | 0 | 0 | 0.13172 | 0.13172 | 0.13172 | 0 | 0.1015 | 0.1015 | 0.1015 | 0 | 0 | 0 | 0.073303 | 0.021622 | 0.5 | 0.84
0.75 | 1.05 | 0.28818 | 0.26607 | 0 | 0 | 0 | 0 | 0.23117 | 0.23117 | 0.23117 | 0 | 0.18745 | 0.18745 | 0.18745 | 0 | 0 | 0 | 0.12752 | 0.064131 | 0.75 | 1.05
1 | 1.315 | 0.4781 | 0.40973 | 0 | 0 | 0 | 0 | 0.37466 | 0.37466 | 0.37466 | 0 | 0.31182 | 0.31182 | 0.31182 | 0 | 0 | 0 | 0.22615 | 0.12216 | 1 | 1.315
1.25 | 1.66 | 0.79702 | 0.70797 | 0 | 0 | 0 | 0 | 0.6484 | 0.6484 | 0.6484 | 0 | 0.55609 | 0.55609 | 0.55609 | 0 | 0 | 0 | 0.45814 | 0.27334 | 1.25 | 1.66
1.5 | 1.9 | 1.0667 | 0.96325 | 0 | 0 | 0 | 0 | 0.88255 | 0.88255 | 0.88255 | 0 | 0.76607 | 0.76607 | 0.76607 | 0 | 0 | 0 | 0.60953 | 0.41198 | 1.5 | 1.9
2 | 2.375 | 1.716 | 1.5841 | 0 | 0 | 0 | 0 | 1.4547 | 1.4547 | 1.4547 | 0 | 1.2801 | 1.2801 | 1.2801 | 0 | 0 | 0 | 0.96898 | 0.76914 | 2 | 2.375
2.5 | 2.875 | 2.4986 | 2.364 | 0 | 0 | 0 | 0 | 2.0755 | 2.0755 | 2.0755 | 0 | 1.8373 | 1.8373 | 1.8373 | 0 | 0 | 0 | 1.5375 | 1.0679 | 2.5 | 2.875
3 | 3.5 | 3.7846 | 3.6184 | 0 | 0 | 0 | 0 | 3.2048 | 3.2048 | 3.2048 | 0 | 2.8634 | 2.8634 | 2.8634 | 0 | 0 | 0 | 2.3443 | 1.8011 | 3 | 3.5
3.5 | 4 | 5.0048 | 4.8135 | 0 | 0 | 0 | 0 | 4.286 | 4.286 | 4.286 | 0 | 3.853 | 3.853 | 3.853 | 0 | 0 | 0 | 0 | 0 | 3.5 | 4
4 | 4.5 | 6.3953 | 6.1788 | 0 | 5.7906 | 0 | 0 | 5.5187 | 5.5187 | 5.5187 | 0 | 4.984 | 4.984 | 4.984 | 0 | 4.4716 | 0 | 4.0244 | 3.3827 | 4 | 4.5
5 | 5.563 | 9.7271 | 9.5459 | 0 | 0 | 0 | 0 | 8.6727 | 8.6727 | 8.6727 | 0 | 7.8871 | 7.8871 | 7.8871 | 0 | 7.089 | 0 | 6.3335 | 5.6206 | 5 | 5.563
6 | 6.625 | 13.9764 | 13.7591 | 0 | 13.0331 | 0 | 0 | 12.5241 | 12.5241 | 12.5241 | 0 | 11.3001 | 11.3001 | 11.3001 | 0 | 10.3031 | 0 | 9.1605 | 8.1648 | 6 | 6.625
8 | 8.625 | 24.064 | 23.7331 | 0 | 22.821 | 22.4767 | 22.1789 | 21.6871 | 21.6871 | 21.6871 | 20.7836 | 19.7955 | 19.7955 | 19.7955 | 18.8314 | 17.5866 | 16.6881 | 15.8038 | 16.0928 | 8 | 8.625
10 | 10.75 | 37.4088 | 36.9676 | 0 | 36.2053 | 35.7712 | 34.9799 | 34.1839 | 34.1839 | 34.1839 | 32.3665 | 32.3665 | 32.3665 | 31.1303 | 29.5238 | 27.9598 | 26.0677 | 24.5994 | 26.0677 | 10 | 10.75
12 | 12.75 | 52.6729 | 52.2671 | 0 | 51.0926 | 51.0926 | 49.7667 | 49.0285 | 49.0285 | 48.5232 | 46.02 | 47.0069 | 47.0069 | 44.0466 | 41.6633 | 39.3462 | 37.5374 | 34.911 | 39.3462 | 12 | 12.75
14 | 14 | 63.792 | 63.1968 | 62.0517 | 62.0517 | 60.917 | 59.7747 | 59.7747 | 0 | 58.6433 | 55.8882 | 57.5404 | 0 | 53.1993 | 50.047 | 47.5043 | 45.0279 | 42.6178 | 0 | 14 | 14
16 | 16 | 83.6034 | 83.1133 | 81.7993 | 81.7993 | 80.4957 | 79.1818 | 79.1818 | 0 | 76.607 | 73.4533 | 76.607 | 0 | 69.7407 | 66.1435 | 62.6229 | 58.6433 | 55.8882 | 0 | 16 | 16
18 | 18 | 106.3063 | 105.7535 | 104.2706 | 104.2706 | 102.7982 | 99.8381 | 101.3128 | 0 | 96.9672 | 92.6945 | 98.3974 | 0 | 88.518 | 83.7956 | 79.1818 | 75.3457 | 70.9741 | 0 | 18 | 18
20 | 20 | 131.1176 | 130.3171 | 129.4658 | 129.4658 | 126.1675 | 122.9117 | 126.1675 | 0 | 120.4914 | 114.9709 | 122.9117 | 0 | 109.5554 | 103.5331 | 98.3974 | 92.6945 | 87.8386 | 0 | 20 | 20
22 | 22 | 159.2055 | 158.3232 | 157.3848 | 157.3848 | 153.746 | 150.1497 | 153.746 | 0 | 0 | 139.6163 | 150.1497 | 0 | 132.8067 | 126.1675 | 119.6984 | 113.3996 | 107.2711 | 0 | 22 | 22
24 | 24 | 189.0532 | 188.0276 | 188.0276 | 188.0276 | 184.0483 | 178.1747 | 184.0483 | 0 | 174.2708 | 165.7203 | 180.1116 | 0 | 158.3232 | 149.2644 | 141.3591 | 134.5067 | 126.9815 | 0 | 24 | 24
26 | 26 | 0 | 0 | 219.2463 | 0 | 212.7972 | 0 | 217.0744 | 0 | 0 | 0 | 212.7972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26
28 | 28 | 0 | 0 | 255.1678 | 0 | 248.2067 | 243.6315 | 252.8244 | 0 | 0 | 0 | 248.2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 28
30 | 30 | 296.2989 | 293.8132 | 293.8132 | 0 | 286.3399 | 281.4243 | 291.2981 | 0 | 0 | 0 | 286.3399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30
32 | 32 | 0 | 0 | 335.1823 | 0 | 327.197 | 321.9409 | 332.4957 | 0 | 319.308 | 0 | 327.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32
34 | 34 | 0 | 0 | 379.2753 | 0 | 370.7779 | 365.1813 | 376.417 | 0 | 362.3768 | 0 | 370.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
36 | 36 | 0 | 0 | 426.092 | 0 | 417.0826 | 411.1455 | 423.0622 | 0 | 405.251 | 0 | 417.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 579.3404 | 0 | 0 | 0 | 572.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 42

## HDPE Pipe Dimensions
SMART DOG MININGTM
It takes a smart dog to find hidden treasures
To use enter the required data |  | in the highlighted cells | [5 empty] | William & Hazen Coefficient (C)
To Obtain the Dimensions of a Pipe | [6 empty] | High | Aveage | Low | Design
Enter Nominal Pipe Diameter & Pipe Schedule |  |  |  |  | Cement Lined or Cement |  | 160 | 150 | 140 | 140
Enter Nominal Pipe Diameter, Pipe Schedule, Flow (g.min), & C Factor |  |  |  |  | Fibre |  | 160 | 150 | 140 | 140
[5 empty] | Copper, Brass, glass |  | 150 | 140 | 120 | 130
Nominal Pipe Diameter |  | 22 |  |  | Wood stave |  | 145 | 120 | 110 | 110
Pipe Schedule |  | 17 |  |  | Seamless Steel |  | 150 | 140 | 80 | 100
Flow | Q | 8346 | g/min |  | Iron |  | 150 | 130 | 80 | 100
C Factor | C | 140 |  |  | Tar Coated |  | 145 | 130 | 80 | 100
Head Loss (ft/100ft) | S | 1.0706 | Feet |  | Concrete |  | 152 | 120 | 85 | 100
Velocity | V | 9.0474 | Ft/sec |  | Corrugated Steel |  |  |  | 60 | 60
Velocity Head |  | 1.2688 | Feet |  | HDPE/PE/PVC |  |  |  |  | 140
Outside Diameter |  | 22 | inches
Wall Thickness |  | 1.294 | inches
Inside diameter | D | 19.412 | inches
Flow Area | A | 295.9582 | inches^2
Weight of Pipe |  | 36.805 | lb/foot
Weight of Water |  | 128.3 | lb/foot
Total Weight |  | 165.105 | lb/foot
WALL THICKNESS
Nominal | Outside | [5 empty] | (inches) | [5 empty] | Nominal | Outside
Diameter | Diameter | 7 | 7.3 | 9 | 11 | 13.5 | 15.5 | 17 | 19 | 21 | 26 | 32.5 | Diameter | Diameter
0.75 | 1.05 | 0.15 | 0.144 | 0.117 | 0.095 | [7 empty] | 0.75 | 1.05
1 | 1.315 | 0.188 | 0.18 | 0.146 | 0.12 | [7 empty] | 1 | 1.315
1.25 | 1.66 | 0.237 | 0.227 | 0.184 | 0.151 | [7 empty] | 1.25 | 1.66
1.5 | 1.9 | 0.271 | 0.26 | 0.211 | 0.173 | [7 empty] | 1.5 | 1.9
2 | 2.375 | 0.339 | 0.325 | 0.264 | 0.216 | 0.176 | 0.153 | 0.14 |  |  |  |  | 2 | 2.375
3 | 3.5 | 0.5 | 0.479 | 0.389 | 0.318 | 0.259 | 0.226 | 0.206 |  |  |  |  | 3 | 3.5
4 | 4.5 | 0.643 | 0.616 | 0.5 | 0.409 | 0.333 | 0.29 | 0.265 | 0.237 | 0.214 | 0.173 | 0.138 | 4 | 4.5
5 | 5.375 | 0.768 | 0.736 | 0.597 | 0.489 | 0.398 | 0.347 | 0.316 | 0.283 | 0.256 | 0.207 | 0.165 | 5 | 5.375
5 | 5.563 | 0.795 | 0.762 | 0.618 | 0.506 | 0.412 | 0.359 | 0.327 | 0.293 | 0.265 | 0.214 | 0.171 | 5 | 5.563
6 | 6.625 | 0.946 | 0.908 | 0.736 | 0.602 | 0.491 | 0.427 | 0.39 | 0.349 | 0.315 | 0.255 | 0.204 | 6 | 6.625
7 | 7.125 | 1.018 | 0.976 | 0.792 | 0.648 | 0.528 | 0.46 | 0.419 | 0.375 | 0.339 | 0.274 | 0.219 | 7 | 7.125
8 | 8.625 | 1.232 | 1.182 | 0.958 | 0.784 | 0.639 | 0.556 | 0.507 | 0.454 | 0.411 | 0.332 | 0.265 | 8 | 8.625
10 | 10.75 | 1.536 | 1.473 | 1.194 | 0.977 | 0.796 | 0.694 | 0.632 | 0.566 | 0.512 | 0.413 | 0.331 | 10 | 10.75
12 | 12.75 | 1.821 | 1.747 | 1.417 | 1.159 | 0.944 | 0.823 | 0.75 | 0.671 | 0.607 | 0.49 | 0.392 | 12 | 12.75
14 | 14 | 2 | 1.918 | 1.556 | 1.273 | 1.037 | 0.903 | 0.824 | 0.737 | 0.667 | 0.538 | 0.431 | 14 | 14
16 | 16 | 2.286 | 2.192 | 1.778 | 1.455 | 1.185 | 1.032 | 0.941 | 0.842 | 0.762 | 0.615 | 0.492 | 16 | 16
18 | 18 | 2.571 | 2.466 | 2 | 1.636 | 1.333 | 1.161 | 1.059 | 0.947 | 0.857 | 0.692 | 0.554 | 18 | 18
20 | 20 | 2.857 | 2.74 | 2.222 | 1.818 | 1.481 | 1.29 | 1.176 | 1.053 | 0.952 | 0.769 | 0.615 | 20 | 20
22 | 22 | 3.143 | 3.014 | 2.444 | 2 | 1.63 | 1.419 | 1.294 | 1.158 | 1.048 | 0.846 | 0.677 | 22 | 22
24 | 24 | 3.429 | 3.288 | 2.667 | 2.182 | 1.778 | 1.548 | 1.412 | 1.263 | 1.143 | 0.923 | 0.738 | 24 | 24
26 | 26 |  | 3.562 | 2.889 | 2.364 | 1.926 | 1.677 | 1.529 | 1.368 | 1.238 | 1 | 0.8 | 26 | 26
28 | 28 |  |  | 3.111 | 2.545 | 2.074 | 1.806 | 1.647 | 1.474 | 1.333 | 1.077 | 0.862 | 28 | 28
30 | 30 |  |  | 3.333 | 2.727 | 2.222 | 1.935 | 1.765 | 1.579 | 1.429 | 1.154 | 0.923 | 30 | 30
32 | 32 |  |  | 3.556 | 2.909 | 2.37 | 2.065 | 1.882 | 1.684 | 1.524 | 1.231 | 0.985 | 32 | 32
34 | 34 |  |  |  | 3.091 | 2.519 | 2.194 | 2 | 1.789 | 1.619 | 1.308 | 1.046 | 34 | 34
36 | 36 |  |  |  | 3.273 | 2.667 | 2.323 | 2.118 | 1.895 | 1.714 | 1.385 | 1.108 | 36 | 36
42 | 42 |  |  |  |  | 3.111 | 2.71 | 2.471 | 2.211 | 2 | 1.615 | 1.292 | 42 | 42
48 | 48 |  |  |  |  | 3.556 | 3.097 | 2.824 | 2.526 | 2.286 | 1.846 | 1.477 | 48 | 48
54 | 54 | [5 empty] | 3.484 | 3.176 | 2.842 | 2.571 | 2.077 | 1.662 | 54 | 54
63 | 62.99 | [8 empty] | 3 | 2.423 | 1.938 | 63 | 62.99
INSIDE DIAMETER
Nominal | Outside | [5 empty] | (inches) | [5 empty] | Nominal | Outside
Diameter | Diameter | 7 | 7.3 | 9 | 11 | 13.5 | 15.5 | 17 | 19 | 21 | 26 | 32.5 | Diameter | Diameter
0.75 | 1.05 | 0.75 | 0.762 | 0.816 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 1.05
1 | 1.315 | 0.939 | 0.955 | 1.023 | 1.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.315
1.25 | 1.66 | 1.186 | 1.206 | 1.292 | 1.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.66
1.5 | 1.9 | 1.358 | 1.38 | 1.478 | 1.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.9
2 | 2.375 | 1.697 | 1.725 | 1.847 | 1.943 | 2.023 | 2.069 | 2.095 | 0 | 0 | 0 | 0 | 2 | 2.375
3 | 3.5 | 2.5 | 2.542 | 2.722 | 2.864 | 2.982 | 3.048 | 3.088 | 0 | 0 | 0 | 0 | 3 | 3.5
4 | 4.5 | 3.214 | 3.268 | 3.5 | 3.682 | 3.834 | 3.92 | 3.97 | 4.026 | 4.072 | 4.154 | 4.224 | 4 | 4.5
5 | 5.375 | 3.839 | 3.903 | 4.181 | 4.397 | 4.579 | 4.681 | 4.743 | 4.809 | 4.863 | 4.961 | 5.045 | 5 | 5.375
5 | 5.563 | 3.973 | 4.039 | 4.327 | 4.551 | 4.739 | 4.845 | 4.909 | 4.977 | 5.033 | 5.135 | 5.221 | 5 | 5.563
6 | 6.625 | 4.733 | 4.809 | 5.153 | 5.421 | 5.643 | 5.771 | 5.845 | 5.927 | 5.995 | 6.115 | 6.217 | 6 | 6.625
7 | 7.125 | 5.089 | 5.173 | 5.541 | 5.829 | 6.069 | 6.205 | 6.287 | 6.375 | 6.447 | 6.577 | 6.687 | 7 | 7.125
8 | 8.625 | 6.161 | 6.261 | 6.709 | 7.057 | 7.347 | 7.513 | 7.611 | 7.717 | 7.803 | 7.961 | 8.095 | 8 | 8.625
10 | 10.75 | 7.678 | 7.804 | 8.362 | 8.796 | 9.158 | 9.362 | 9.486 | 9.618 | 9.726 | 9.924 | 10.088 | 10 | 10.75
12 | 12.75 | 9.108 | 9.256 | 9.916 | 10.432 | 10.862 | 11.104 | 11.25 | 11.408 | 11.536 | 11.77 | 11.966 | 12 | 12.75
14 | 14 | 10 | 10.164 | 10.888 | 11.454 | 11.926 | 12.194 | 12.352 | 12.526 | 12.666 | 12.924 | 13.138 | 14 | 14
16 | 16 | 11.428 | 11.616 | 12.444 | 13.09 | 13.63 | 13.936 | 14.118 | 14.316 | 14.476 | 14.77 | 15.016 | 16 | 16
18 | 18 | 12.858 | 13.068 | 14 | 14.728 | 15.334 | 15.678 | 15.882 | 16.106 | 16.286 | 16.616 | 16.892 | 18 | 18
20 | 20 | 14.286 | 14.52 | 15.556 | 16.364 | 17.038 | 17.42 | 17.648 | 17.894 | 18.096 | 18.462 | 18.77 | 20 | 20
22 | 22 | 15.714 | 15.972 | 17.112 | 18 | 18.74 | 19.162 | 19.412 | 19.684 | 19.904 | 20.308 | 20.646 | 22 | 22
24 | 24 | 17.142 | 17.424 | 18.666 | 19.636 | 20.444 | 20.904 | 21.176 | 21.474 | 21.714 | 22.154 | 22.524 | 24 | 24
26 | 26 | 0 | 18.876 | 20.222 | 21.272 | 22.148 | 22.646 | 22.942 | 23.264 | 23.524 | 24 | 24.4 | 26 | 26
28 | 28 | 0 | 0 | 21.778 | 22.91 | 23.852 | 24.388 | 24.706 | 25.052 | 25.334 | 25.846 | 26.276 | 28 | 28
30 | 30 | 0 | 0 | 23.334 | 24.546 | 25.556 | 26.13 | 26.47 | 26.842 | 27.142 | 27.692 | 28.154 | 30 | 30
32 | 32 | 0 | 0 | 24.888 | 26.182 | 27.26 | 27.87 | 28.236 | 28.632 | 28.952 | 29.538 | 30.03 | 32 | 32
34 | 34 | 0 | 0 | 0 | 27.818 | 28.962 | 29.612 | 30 | 30.422 | 30.762 | 31.384 | 31.908 | 34 | 34
36 | 36 | 0 | 0 | 0 | 29.454 | 30.666 | 31.354 | 31.764 | 32.21 | 32.572 | 33.23 | 33.784 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 35.778 | 36.58 | 37.058 | 37.578 | 38 | 38.77 | 39.416 | 42 | 42
48 | 48 | 0 | 0 | 0 | 0 | 40.888 | 41.806 | 42.352 | 42.948 | 43.428 | 44.308 | 45.046 | 48 | 48
54 | 54 | 0 | 0 | 0 | 0 | 0 | 47.032 | 47.648 | 48.316 | 48.858 | 49.846 | 50.676 | 54 | 54
63 | 62.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.99 | 58.144 | 59.114 | 63 | 62.99
FLOW AREA
Nominal | Outside | [5 empty] | (inches) | [5 empty] | Nominal | Outside
Diameter | Diameter | 7 | 7.3 | 9 | 11 | 13.5 | 15.5 | 17 | 19 | 21 | 26 | 32.5 | Diameter | Diameter
0.75 | 1.05 | 0.44179 | 0.45604 | 0.52296 | 0.58088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 1.05
1 | 1.315 | 0.6925 | 0.7163 | 0.82194 | 0.90763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.315
1.25 | 1.66 | 1.1047 | 1.1423 | 1.311 | 1.4484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.66
1.5 | 1.9 | 1.4484 | 1.4957 | 1.7157 | 1.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.9
2 | 2.375 | 2.2618 | 2.3371 | 2.6793 | 2.9651 | 3.2143 | 3.3621 | 3.4471 | 0 | 0 | 0 | 0 | 2 | 2.375
3 | 3.5 | 4.9087 | 5.0751 | 5.8192 | 6.4422 | 6.984 | 7.2966 | 7.4894 | 0 | 0 | 0 | 0 | 3 | 3.5
4 | 4.5 | 8.113 | 8.3879 | 9.6211 | 10.6477 | 11.545 | 12.0687 | 12.3786 | 12.7303 | 13.0228 | 13.5526 | 14.0132 | 4 | 4.5
5 | 5.375 | 11.5751 | 11.9643 | 13.7294 | 15.1846 | 16.4676 | 17.2095 | 17.6684 | 18.1635 | 18.5737 | 19.3298 | 19.99 | 5 | 5.375
5 | 5.563 | 12.3973 | 12.8126 | 14.705 | 16.2669 | 17.6386 | 18.4365 | 18.9267 | 19.4547 | 19.895 | 20.7096 | 21.409 | 5 | 5.563
6 | 6.625 | 17.5939 | 18.1635 | 20.855 | 23.0807 | 25.0098 | 26.1572 | 26.8324 | 27.5905 | 28.2272 | 29.3686 | 30.3565 | 6 | 6.625
7 | 7.125 | 20.3402 | 21.0172 | 24.1138 | 26.6857 | 28.9284 | 30.2394 | 31.0439 | 31.9191 | 32.6441 | 33.9739 | 35.1198 | 7 | 7.125
8 | 8.625 | 29.8121 | 30.7877 | 35.3513 | 39.1138 | 42.3945 | 44.3319 | 45.496 | 46.7721 | 47.8204 | 49.7766 | 51.4664 | 8 | 8.625
10 | 10.75 | 46.3005 | 47.8326 | 54.9174 | 60.766 | 65.8705 | 68.8378 | 70.6734 | 72.654 | 74.2948 | 77.3505 | 79.9282 | 10 | 10.75
12 | 12.75 | 65.1532 | 67.2878 | 77.2259 | 85.4722 | 92.6637 | 96.8387 | 99.402 | 102.2137 | 104.5202 | 108.8035 | 112.4574 | 12 | 12.75
14 | 14 | 78.5398 | 81.137 | 93.1078 | 103.0396 | 111.7068 | 116.7837 | 119.8297 | 123.2295 | 125.9995 | 131.1849 | 135.5653 | 14 | 14
16 | 16 | 102.5724 | 105.9749 | 121.6214 | 134.5765 | 145.9088 | 152.5338 | 156.5439 | 160.9657 | 164.5838 | 171.3369 | 177.0918 | 16 | 16
18 | 18 | 129.8484 | 134.1245 | 153.938 | 170.3638 | 184.6719 | 193.0506 | 198.1072 | 203.7348 | 208.3141 | 216.8417 | 224.1052 | 18 | 18
20 | 20 | 160.2918 | 165.5858 | 190.0578 | 210.3143 | 227.9959 | 238.3341 | 244.6138 | 251.4808 | 257.1906 | 267.6994 | 276.7059 | 20 | 20
22 | 22 | 193.9382 | 200.3588 | 229.9807 | 254.469 | 275.8221 | 288.3843 | 295.9582 | 304.3103 | 311.1506 | 323.9099 | 334.7817 | 22 | 22
24 | 24 | 230.7878 | 238.4436 | 273.6481 | 302.8279 | 328.2628 | 343.2011 | 352.1906 | 362.1728 | 370.3135 | 385.4732 | 398.4565 | 24 | 24
26 | 26 | 0 | 279.84 | 321.1723 | 355.3911 | 385.2644 | 402.7846 | 413.3828 | 425.0682 | 434.6225 | 452.3893 | 467.5947 | 26 | 26
28 | 28 | 0 | 0 | 372.4996 | 412.2304 | 446.8271 | 467.1348 | 479.3964 | 492.918 | 504.0776 | 524.6583 | 542.261 | 28 | 28
30 | 30 | 0 | 0 | 427.6301 | 473.2072 | 512.9507 | 536.2517 | 550.2978 | 565.8739 | 578.5935 | 602.2801 | 622.5441 | 30 | 30
32 | 32 | 0 | 0 | 486.4855 | 538.3882 | 583.6353 | 610.0477 | 626.1757 | 643.8627 | 658.3351 | 685.2547 | 708.2728 | 32 | 32
34 | 34 | 0 | 0 | 0 | 607.7734 | 658.79 | 688.6925 | 706.8583 | 726.8845 | 743.2228 | 773.5822 | 799.6299 | 34 | 34
36 | 36 | 0 | 0 | 0 | 681.3628 | 738.5912 | 772.104 | 792.4288 | 814.8381 | 833.2565 | 867.2625 | 896.421 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 1005.3609 | 1050.9385 | 1078.5837 | 1109.0655 | 1134.1149 | 1180.5421 | 1220.2111 | 42 | 42
48 | 48 | 0 | 0 | 0 | 0 | 1313.0511 | 1372.6731 | 1408.7623 | 1448.691 | 1481.254 | 1541.8928 | 1593.6845 | 48 | 48
54 | 54 | 0 | 0 | 0 | 0 | 0 | 1737.3078 | 1783.1145 | 1833.4616 | 1874.8272 | 1951.4189 | 2016.9472 | 54 | 54
63 | 62.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2550.8634 | 2655.215 | 2744.5464 | 63 | 62.99
AREA OF HDPE
Nominal | Outside | [5 empty] | (square inches) | [5 empty] | Nominal | Outside
Diameter | Diameter | 7 | 7.3 | 9 | 11 | 13.5 | 15.5 | 17 | 19 | 21 | 26 | 32.5 | Diameter | Diameter
0.75 | 1.05 | 0.42412 | 0.40986 | 0.34294 | 0.28502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 1.05
1 | 1.315 | 0.66563 | 0.64183 | 0.53619 | 0.4505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.315
1.25 | 1.66 | 1.0595 | 1.0219 | 0.85321 | 0.71584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.66
1.5 | 1.9 | 1.3869 | 1.3396 | 1.1196 | 0.93862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.9
2 | 2.375 | 2.1683 | 2.0931 | 1.7508 | 1.4651 | 1.2159 | 1.068 | 0.983 | 0 | 0 | 0 | 0 | 2 | 2.375
3 | 3.5 | 4.7124 | 4.5461 | 3.8019 | 3.1789 | 2.6371 | 2.3245 | 2.1318 | 0 | 0 | 0 | 0 | 3 | 3.5
4 | 4.5 | 7.7913 | 7.5164 | 6.2832 | 5.2566 | 4.3593 | 3.8356 | 3.5257 | 3.174 | 2.8815 | 2.3517 | 1.8911 | 4 | 4.5
5 | 5.375 | 11.1155 | 10.7264 | 8.9613 | 7.5061 | 6.223 | 5.4812 | 5.0223 | 4.5271 | 4.1169 | 3.3608 | 2.7007 | 5 | 5.375
5 | 5.563 | 11.9084 | 11.4931 | 9.6007 | 8.0388 | 6.6671 | 5.8692 | 5.3789 | 4.851 | 4.4107 | 3.5961 | 2.8966 | 5 | 5.563
6 | 6.625 | 16.8777 | 16.3081 | 13.6166 | 11.3909 | 9.4618 | 8.3144 | 7.6393 | 6.8811 | 6.2444 | 5.103 | 4.1151 | 6 | 6.625
7 | 7.125 | 19.531 | 18.854 | 15.7574 | 13.1856 | 10.9428 | 9.6318 | 8.8273 | 7.9522 | 7.2271 | 5.8973 | 4.7514 | 7 | 7.125
8 | 8.625 | 28.6142 | 27.6386 | 23.075 | 19.3125 | 16.0317 | 14.0943 | 12.9302 | 11.6542 | 10.6059 | 8.6497 | 6.9599 | 8 | 8.625
10 | 10.75 | 44.462 | 42.9299 | 35.8451 | 29.9966 | 24.892 | 21.9247 | 20.0892 | 18.1086 | 16.4678 | 13.412 | 10.8344 | 10 | 10.75
12 | 12.75 | 62.5231 | 60.3885 | 50.4504 | 42.2041 | 35.0126 | 30.8376 | 28.2743 | 25.4626 | 23.1561 | 18.8728 | 15.2189 | 12 | 12.75
14 | 14 | 75.3982 | 72.801 | 60.8302 | 50.8984 | 42.2313 | 37.1543 | 34.1083 | 30.7085 | 27.9385 | 22.7532 | 18.3728 | 14 | 14
16 | 16 | 98.4896 | 95.087 | 79.4406 | 66.4854 | 55.1531 | 48.5281 | 44.518 | 40.0963 | 36.4782 | 29.725 | 23.9702 | 16 | 16
18 | 18 | 124.6206 | 120.3445 | 100.531 | 84.1052 | 69.7971 | 61.4184 | 56.3618 | 50.7342 | 46.1549 | 37.6273 | 30.3638 | 18 | 18
20 | 20 | 153.8675 | 148.5735 | 124.1014 | 103.845 | 86.1633 | 75.8252 | 69.5455 | 62.6785 | 56.9687 | 46.4599 | 37.4534 | 20 | 20
22 | 22 | 186.1945 | 179.7739 | 150.152 | 125.6637 | 104.3106 | 91.7485 | 84.1745 | 75.8225 | 68.9821 | 56.2228 | 45.351 | 22 | 22
24 | 24 | 221.6015 | 213.9458 | 178.7413 | 149.5614 | 124.1266 | 109.1882 | 100.1988 | 90.2166 | 82.0758 | 66.9161 | 53.9328 | 24 | 24
26 | 26 | 0 | 251.0891 | 209.7568 | 175.5381 | 145.6647 | 128.1445 | 117.5463 | 105.8609 | 96.3066 | 78.5398 | 63.3345 | 26 | 26
28 | 28 | 0 | 0 | 243.2525 | 203.5217 | 168.9251 | 148.6173 | 136.3558 | 122.8341 | 111.6745 | 91.0938 | 73.4911 | 28 | 28
30 | 30 | 0 | 0 | 279.2282 | 233.6512 | 193.9076 | 170.6066 | 156.5606 | 140.9845 | 128.2648 | 104.5782 | 84.3143 | 30 | 30
32 | 32 | 0 | 0 | 317.7622 | 265.8595 | 220.6124 | 194.2 | 178.072 | 160.385 | 145.9126 | 118.993 | 95.9749 | 32 | 32
34 | 34 | 0 | 0 | 0 | 300.1469 | 249.1303 | 219.2278 | 201.0619 | 181.0358 | 164.6975 | 134.3381 | 108.2903 | 34 | 34
36 | 36 | 0 | 0 | 0 | 336.5132 | 279.2848 | 245.772 | 225.4472 | 203.0379 | 184.6195 | 150.6135 | 121.455 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 380.0814 | 334.5039 | 306.8587 | 276.3768 | 251.3274 | 204.9002 | 165.2312 | 42 | 42
48 | 48 | 0 | 0 | 0 | 0 | 496.5063 | 436.8843 | 400.795 | 360.8663 | 328.3034 | 267.6646 | 215.8729 | 48 | 48
54 | 54 | 0 | 0 | 0 | 0 | 0 | 552.9132 | 507.1065 | 456.7594 | 415.3938 | 338.8021 | 273.2738 | 54 | 54
63 | 62.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565.3924 | 461.0408 | 371.7094 | 63 | 62.99
WEIGHT OF PIPE
Nominal | Outside | [5 empty] | (pounds/foot | [5 empty] | Nominal | Outside
Diameter | Diameter | 7 | 7.3 | 9 | 11 | 13.5 | 15.5 | 17 | 19 | 21 | 26 | 32.5 | Diameter | Diameter
0.75 | 1.05 | 0.184 | 0.178 | 0.15 | 0.125 | [7 empty] | 0.75 | 1.05
1 | 1.315 | 0.289 | 0.279 | 0.234 | 0.197 | [7 empty] | 1 | 1.315
1.25 | 1.66 | 0.46 | 0.444 | 0.372 | 0.312 | [7 empty] | 1.25 | 1.66
1.5 | 1.9 | 0.603 | 0.582 | 0.488 | 0.409 | [7 empty] | 1.5 | 1.9
2 | 2.375 | 0.943 | 0.762 | 0.762 | 0.639 | 0.531 | 0.467 | 0.429 |  |  |  |  | 2 | 2.375
3 | 3.5 | 2.047 | 1.656 | 1.656 | 1.387 | 1.153 | 1.015 | 0.932 |  |  |  |  | 3 | 3.5
4 | 4.5 | 3.384 | 2.737 | 2.737 | 2.294 | 1.906 | 1.678 | 1.54 | 1.387 | 1.262 | 1.03 | 0.831 | 4 | 4.5
5 | 5.375 | 4.83 | 4.663 | 3.903 | 3.272 | 2.718 | 2.396 | 2.197 | 1.98 | 1.801 | 1.47 | 1.186 | 5 | 5.375
5 | 5.563 | 5.172 | 4.182 | 4.182 | 3.505 | 2.912 | 2.564 | 2.353 | 2.12 | 1.929 | 1.574 | 1.27 | 5 | 5.563
6 | 6.625 | 7.336 | 5.932 | 5.932 | 4.971 | 4.13 | 3.637 | 3.338 | 3.007 | 2.736 | 2.233 | 1.801 | 6 | 6.625
7 | 7.125 | 8.195 | 8.2 | 6.863 | 5.75 | 4.779 | 3.985 | 3.86 | 3.478 | 3.165 | 2.582 | 2.083 | 7 | 7.125
8 | 8.625 | 12.433 | 10.054 | 10.054 | 8.425 | 7.001 | 6.164 | 5.657 | 5.097 | 4.637 | 3.784 | 3.053 | 8 | 8.625
10 | 10.75 | 19.314 | 15.618 | 15.618 | 13.089 | 10.875 | 9.576 | 8.788 | 7.918 | 7.204 | 5.878 | 4.742 | 10 | 10.75
12 | 12.75 | 27.17 | 21.97 | 21.97 | 18.412 | 15.298 | 13.471 | 12.362 | 11.138 | 10.134 | 8.269 | 6.671 | 12 | 12.75
14 | 14 | 32.758 | 26.489 | 26.489 | 22.199 | 18.445 | 16.242 | 14.905 | 13.429 | 12.218 | 9.97 | 8.044 | 14 | 14
16 | 16 | 42.786 | 34.598 | 34.598 | 28.994 | 24.092 | 21.214 | 19.467 | 17.54 | 15.959 | 13.022 | 10.506 | 16 | 16
18 | 18 | 54.151 | 43.788 | 43.788 | 36.696 | 30.491 | 26.849 | 24.638 | 22.199 | 20.198 | 16.48 | 13.296 | 18 | 18
20 | 20 | 66.853 | 54.059 | 54.059 | 45.304 | 37.643 | 33.146 | 30.418 | 27.406 | 24.936 | 20.346 | 16.415 | 20 | 20
22 | 22 | 80.17 | 65.412 | 65.412 | 54.818 | 45.548 | 40.107 | 36.805 | 33.162 | 30.172 | 24.619 | 19.863 | 22 | 22
24 | 24 | 96.267 | 92.988 | 77.845 | 65.237 | 54.206 | 47.731 | 43.801 | 39.465 | 35.907 | 29.299 | 23.638 | 24 | 24
26 | 26 |  | 110.192 | 92.05 | 76.563 | 63.617 | 56.018 | 51.406 | 46.316 | 42.141 | 34.385 | 27.742 | 26 | 26
28 | 28 |  |  | 106.75 | 88.795 | 73.781 | 64.967 | 59.618 | 53.716 | 48.874 | 39.879 | 32.174 | 28 | 28
30 | 30 |  |  | 121.633 | 101.934 | 84.697 | 74.58 | 68.439 | 61.664 | 56.105 | 45.779 | 36.934 | 30 | 30
32 | 32 |  |  | 139.452 | 116.67 | 96.367 | 84.855 | 77.869 | 70.16 | 63.835 | 52.086 | 42.023 | 32 | 32
34 | 34 |  |  |  | 130.93 | 109.332 | 96.209 | 87.907 | 79.204 | 72.064 | 58.814 | 47.44 | 34 | 34
36 | 36 |  |  |  | 146.78 | 121.96 | 107.395 | 98.553 | 88.796 | 80.791 | 65.922 | 53.186 | 36 | 36
42 | 42 |  |  |  |  | 166.8 | 146.176 | 134.141 | 120.861 | 109.966 | 89.727 | 72.392 | 42 | 42
48 | 48 |  |  |  |  | 217.895 | 175.891 | 175.205 | 157.857 | 143.629 | 117.194 | 94.552 | 48 | 48
54 | 54 | [5 empty] | 242.649 | 222.547 | 199.791 | 182.298 | 148.324 | 119.668 | 54 | 54
63 | 62.99 | [8 empty] | 247.8 | 202.01 | 162.98 | 63 | 62.99
Water | 62.425 | lbs/ft^3 |  |  |  |  | WEIGHT OF WATER
Nominal | Outside | [5 empty] | (pounds/foot) | [5 empty] | Nominal | Outside
Diameter | Diameter | 7 | 7.3 | 9 | 11 | 13.5 | 15.5 | 17 | 19 | 21 | 26 | 32.5 | Diameter | Diameter
0.75 | 1.05 | 0.19152 | 0.1977 | 0.22671 | 0.25182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 1.05
1 | 1.315 | 0.3002 | 0.31052 | 0.35632 | 0.39346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.315
1.25 | 1.66 | 0.47891 | 0.4952 | 0.56834 | 0.62789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.66
1.5 | 1.9 | 0.62789 | 0.6484 | 0.74376 | 0.82222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.9
2 | 2.375 | 0.9805 | 1.0131 | 1.1615 | 1.2854 | 1.3934 | 1.4575 | 1.4944 | 0 | 0 | 0 | 0 | 2 | 2.375
3 | 3.5 | 2.128 | 2.2001 | 2.5227 | 2.7927 | 3.0276 | 3.1631 | 3.2467 | 0 | 0 | 0 | 0 | 3 | 3.5
4 | 4.5 | 3.517 | 3.6362 | 4.1708 | 4.6159 | 5.0048 | 5.2319 | 5.3662 | 5.5187 | 5.6455 | 5.8751 | 6.0748 | 4 | 4.5
5 | 5.375 | 5.0179 | 5.1866 | 5.9518 | 6.5826 | 7.1388 | 7.4604 | 7.6594 | 7.874 | 8.0518 | 8.3796 | 8.6658 | 5 | 5.375
5 | 5.563 | 5.3743 | 5.5544 | 6.3747 | 7.0518 | 7.6464 | 7.9923 | 8.2049 | 8.4338 | 8.6246 | 8.9777 | 9.281 | 5 | 5.563
6 | 6.625 | 7.6271 | 7.874 | 9.0408 | 10.0056 | 10.8419 | 11.3393 | 11.632 | 11.9607 | 12.2367 | 12.7315 | 13.1598 | 6 | 6.625
7 | 7.125 | 8.8176 | 9.1111 | 10.4535 | 11.5684 | 12.5407 | 13.109 | 13.4578 | 13.8371 | 14.1515 | 14.7279 | 15.2247 | 7 | 7.125
8 | 8.625 | 12.9237 | 13.3467 | 15.325 | 16.9561 | 18.3783 | 19.2182 | 19.7228 | 20.276 | 20.7305 | 21.5785 | 22.311 | 8 | 8.625
10 | 10.75 | 20.0716 | 20.7358 | 23.8071 | 26.3425 | 28.5553 | 29.8417 | 30.6374 | 31.496 | 32.2073 | 33.532 | 34.6494 | 10 | 10.75
12 | 12.75 | 28.2444 | 29.1697 | 33.478 | 37.0528 | 40.1703 | 41.9802 | 43.0914 | 44.3103 | 45.3102 | 47.1671 | 48.751 | 12 | 12.75
14 | 14 | 34.0476 | 35.1735 | 40.3629 | 44.6684 | 48.4257 | 50.6265 | 51.947 | 53.4208 | 54.6217 | 56.8696 | 58.7685 | 14 | 14
16 | 16 | 44.4658 | 45.9409 | 52.7237 | 58.3398 | 63.2525 | 66.1245 | 67.8629 | 69.7797 | 71.3482 | 74.2757 | 76.7705 | 16 | 16
18 | 18 | 56.2902 | 58.1439 | 66.7332 | 73.8539 | 80.0565 | 83.6888 | 85.8808 | 88.3205 | 90.3056 | 94.0024 | 97.1512 | 18 | 18
20 | 20 | 69.4876 | 71.7826 | 82.3914 | 91.1727 | 98.8378 | 103.3195 | 106.0418 | 109.0187 | 111.4939 | 116.0495 | 119.9539 | 20 | 20
22 | 22 | 84.0736 | 86.8569 | 99.6982 | 110.3141 | 119.5708 | 125.0166 | 128.3 | 131.9206 | 134.8859 | 140.4172 | 145.1302 | 22 | 22
24 | 24 | 100.0481 | 103.3669 | 118.6283 | 131.278 | 142.3042 | 148.7801 | 152.6771 | 157.0044 | 160.5335 | 167.1053 | 172.7337 | 24 | 24
26 | 26 | 0 | 121.3126 | 139.2304 | 154.0645 | 167.0148 | 174.6099 | 179.2043 | 184.27 | 188.4119 | 196.1139 | 202.7055 | 26 | 26
28 | 28 | 0 | 0 | 161.4812 | 178.7048 | 193.7026 | 202.5062 | 207.8217 | 213.6834 | 218.5211 | 227.443 | 235.0739 | 28 | 28
30 | 30 | 0 | 0 | 185.3806 | 205.1386 | 222.3677 | 232.4688 | 238.5579 | 245.3102 | 250.8243 | 261.0926 | 269.8772 | 30 | 30
32 | 32 | 0 | 0 | 210.8948 | 233.395 | 253.01 | 264.4599 | 271.4515 | 279.1189 | 285.3928 | 297.0627 | 307.0412 | 32 | 32
34 | 34 | 0 | 0 | 0 | 263.474 | 285.59 | 298.553 | 306.428 | 315.1095 | 322.1922 | 335.3533 | 346.6451 | 34 | 34
36 | 36 | 0 | 0 | 0 | 295.3755 | 320.1844 | 334.7124 | 343.5234 | 353.238 | 361.2225 | 375.9643 | 388.6047 | 36 | 36
42 | 42 | 0 | 0 | 0 | 0 | 435.8309 | 455.5891 | 467.5735 | 480.7876 | 491.6467 | 511.7732 | 528.97 | 42 | 42
48 | 48 | 0 | 0 | 0 | 0 | 569.2168 | 595.0633 | 610.7083 | 628.0176 | 642.1339 | 668.4212 | 690.8733 | 48 | 48
54 | 54 | 0 | 0 | 0 | 0 | 0 | 753.135 | 772.9925 | 794.8184 | 812.7506 | 845.9536 | 874.3606 | 54 | 54
63 | 62.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.817 | 1151.0541 | 1189.7799 | 63 | 62.99

## Major Line Sizing
SMART DOG MININGTM
It takes a smart dog to find hidden treasures
Flow |  | g/min | 1500
Major Line Sizing |  |  | Steel | HDPE
Pump Suction Pipes : | d =0.3586*q^0.478 | inches | 12 | 12
Pump Discharge Pipes : | d =0.256*q^0.43 | inches | 6 | 6
Main circuits : | d =0.4803*q^0.41 | inches | 10 | 10
Leads off main circuits : | d =0.4138*q^0.41 | inches | 10 | 10
|  |  | Nominal | Nominal
|  |  | Diameter | Diameter
|  |  | 0.125 | 0.75
|  |  | 0.25 | 1
|  |  | 0.375 | 1.25
|  |  | 0.5 | 1.5
|  |  | 0.75 | 2
|  |  | 1 | 3
|  |  | 1.25 | 4
|  |  | 1.5 | 5
|  |  | 2 | 5
|  |  | 2.5 | 6
|  |  | 3 | 7
|  |  | 3.5 | 8
|  |  | 4 | 10
|  |  | 5 | 12
|  |  | 6 | 14
|  |  | 8 | 16
|  |  | 10 | 18
|  |  | 12 | 20
|  |  | 14 | 22
|  |  | 16 | 24
|  |  | 18 | 26
|  |  | 20 | 28
|  |  | 22 | 30
|  |  | 24 | 32
|  |  | 26 | 34
|  |  | 28 | 36
|  |  | 30 | 42
|  |  | 32 | 48
|  |  | 34 | 54
|  |  | 36 | 63
42

## Weir Calculations
SMART DOG MININGTM
It takes a smart dog to find hidden treasures
To use enter the required data |  |  |  | in the highlighted cells
Rectangular Weir
| Flow | 727.6095 | (g/min)
| Length | 48 | inches
| Head | 3 | inches
Notch Weir
| Flow | 273.7401 | (g/min)
| Length | 48 | inches
| Head | 3 | inches
90 deg Notch Weir
| Flow | 34.1966 | (g/min)
| Head | 3 | inches
60 deg Notch Weir
| Flow | 19.7429 | (g/min)
| Head | 3 | inches

## Orifice-Nozzel Flow
SMART DOG MININGTM
It takes a smart dog to find hidden treasures
d/D |  | >0.3 | <0.3 |  | To use enter the required data | in the highlighted cells
Flow gal/min | Q | 14.2722 | 14.2608 | (g/min)
d/D |  | 0.2
Orifice diameter (inch) | d | .3 | inches
Pipe diameter (inch) | D | 1.5 | inches
Differential head (feet) | h | 175 | feet
Discharge Coefficient | K | .61
Re-entrant Tube (L/D =.5) | K | 0.52
Sharp Edged | K | 0.61
Square Edged (turbulant) | K | 0.61
Re-entrant Tube (L/D =1) | K | 0.73
Square Edged (laminar) | K | 0.82
Well rounded | K | 0.98

## Angle Flanges
SMART DOG MININGTM
It takes a smart dog to find hidden treasures
Standard Angle Flanges
Order Size | Inside Diameter | Height | Width | Gauge | Bolt Circle | Bolt Size | Number of Holes | Approx. Wt. Lbs
6" | 6(1/8)" | 1(1/4)" | 1(1/4)" | 11 GA. | 7(1/2)" | (3/8)" | 6 | 1.6
7" | 7(1/8)" | 1(1/4)" | 1(1/4)" | 11 GA. | 8(1/2)" | (3/8)" | 6 | 1.9
8" | 8(1/8)" | 1(1/4)" | 1(1/4)" | 11 GA. | 9(1/2)" | (3/8)" | 8 | 2.1
9" | 9(1/8)" | 1(1/4)" | 1(1/4)" | 11 GA. | 10(5/8)" | (3/8)" | 6 | 2.4
10" | 10(1/8)" | 1(1/4)" | 1(1/4)" | 11 GA. | 11(1/2)" | (3/8)" | 8 | 2.6
11" | 11(1/8)" | 1(1/4)" | 1(1/4)" | 11 GA. | 12(3/4)" | (3/8)" | 6 | 2.9
12" | 12(3/16)" | 1(1/2)" | 1(1/2)" | 11 GA. | 13(13/16)" | (3/8)" | 12 | 3.9
13" | 13(3/16)" | 1(1/2)" | 1(1/2)" | 11 GA. | 15" | (3/8)" | 8 | 4.2
14" | 14(3/16)" | 1(1/2)" | 1(1/2)" | 11 GA. | 16" | (3/8)" | 8 | 4.5
15" | 15(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 17" | (3/8)" | 8 | 7.1
16" | 16(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 18" | (3/8)" | 8 | 7.5
17" | 17(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 19" | (3/8)" | 8 | 8
18" | 18(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 19(3/4)" | (3/8)" | 8 | 8.4
19" | 19(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 20(3/4)" | (3/8)" | 12 | 8.9
20" | 20(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 21(3/4)" | (3/8)" | 12 | 9.3
21" | 21(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 22(3/4)" | (3/8)" | 12 | 9.8
22" | 22(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 23(3/4)" | (3/8)" | 12 | 10.2
23" | 23(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 24(7/8)" | (3/8)" | 12 | 10.6
24" | 24(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 25(3/4)" | (3/8)" | 8 | 11.1
25" | 25(3/16)" | 1(1/2)" | 1(1/2)" | 7 GA. | 26(7/8)" | (3/8)" | 16 | 11.5
26" | 26(3/16)" | 2" | 2" | 7 GA. | 28(3/8)" | (3/8)" | 16 | 16.1
27" | 27(3/16)" | 2" | 2" | 7 GA. | 29(3/8)" | (3/8)" | 16 | 16.7
28" | 28(3/16)" | 2" | 2" | 7 GA. | 30(3/8)" | (3/8)" | 16 | 17.3
29" | 29(3/16)" | 2" | 2" | 7 GA. | 31(3/8)" | (3/8)" | 16 | 17.9
30" | 30(3/16)" | 2" | 2" | 7 GA. | 32(3/8)" | (3/8)" | 16 | 18.5
31" | 31(3/16)" | 2" | 2" | 7 GA. | 33(3/8)" | (3/8)" | 16 | 19.1
32" | 32(3/16)" | 2" | 2" | 7 GA. | 34(3/8)" | (3/8)" | 16 | 19.7
33" | 33(3/16)" | 2" | 2" | 7 GA. | 35(3/8)" | (3/8)" | 16 | 20.3
34" | 34(3/16)" | 2" | 2" | 7 GA. | 36(3/8)" | (3/8)" | 16 | 20.9
35" | 35(3/16)" | 2" | 2" | 7 GA. | 37(3/8)" | (3/8)" | 16 | 21.5
36" | 36(3/16)" | 2" | 2" | 7 GA. | 38(3/8)" | (3/8)" | 16 | 22.1
37" | 37(3/16)" | 2" | 2" | 7 GA. | 39(3/8)" | (3/8)" | 24 | 22.7
38" | 38(3/16)" | 2" | 2" | 7 GA. | 40(3/8)" | (3/8)" | 24 | 23.3
39" | 39(3/16)" | 2" | 2" | 7 GA. | 41(3/8)" | (3/8)" | 24 | 23.9
40" | 40(3/16)" | 2" | 2" | 7 GA. | 42(3/8)" | (3/8)" | 24 | 24.5
41" | 41(3/16)" | 2" | 2" | 7 GA. | 43(3/8)" | (3/8)" | 24 | 25
42" | 42(3/16)" | 2" | 2" | 7 GA. | 44(3/8)" | (3/8)" | 24 | 25.6
43" | 43(3/16)" | 2" | 2" | 7 GA. | 45(3/8)" | (3/8)" | 24 | 26.2
44" | 44(3/16)" | 2" | 2" | 7 GA. | 46(3/8)" | (3/8)" | 24 | 26.8
45" | 45(3/16)" | 2" | 2" | 7 GA. | 47(3/8)" | (3/8)" | 24 | 27.4
46" | 46(3/16)" | 2" | 2" | 7 GA. | 48(3/8)" | (3/8)" | 24 | 28
47" | 47(3/16)" | 2" | 2" | 7 GA. | 49(3/8)" | (3/8)" | 24 | 28.6
48" | 48(3/16)" | 2" | 2" | 7 GA. | 50(3/8)" | (3/8)" | 24 | 29.2
49" | 49(3/16)" | 2" | 2" | 7 GA. | 51(3/8)" | (3/8)" | 24 | 29.8
50" | 50(3/16)" | 2" | 2" | 7 GA. | 52(3/8)" | (3/8)" | 24 | 30.4
Standard Steel Flanges are available for immediate shipment.
Electro Galvanized Flanges are available with in 3 days.
Stainless Steel and Aluminum Flanges are also available, delivery time and pricing are per quote.

## Pipe Bolting
SMART DOG MININGTM
It takes a smart dog to find hidden treasures
Series 150 Flange Raised Face
Nominal | Flange Bolts |  | Length |  | Gasket
Diameter | Qty | Size | Stud | Mach | ID | OD
0.5 | 4 | 0.5 | 2.25 | 1.75 | 0.625 | 1.875
0.75 | 4 | 0.5 | 2.25 | 2 | 0.8125 | 2.25
1 | 4 | 0.5 | 2.5 | 2 | 1 | 2.625
1.25 | 4 | 0.5 | 2.5 | 2.25 | 1.375 | 3
1.5 | 4 | 0.5 | 2.75 | 2.25 | 1.625 | 3.375
2 | 4 | 0.625 | 3 | 2.75 | 2 | 4.875
2.5 | 4 | 0.625 | 3.25 | 3 | 2.5 | 4.875
3 | 4 | 0.625 | 3.5 | 3 | 3 | 5.375
3.5 | 8 | 0.625 | 3.5 | 3 | 3.5 | 6.375
4 | 8 | 0.625 | 3.5 | 3 | 4 | 6.875
5 | 8 | 0.75 | 3.75 | 3.25 | 5 | 7.75
6 | 8 | 0.75 | 3.75 | 3.25 | 6 | 8.25
8 | 8 | 0.75 | 4 | 3.5 | 8 | 11
10 | 12 | 0.875 | 4.5 | 3.75 | 10 | 13.375
12 | 12 | 0.875 | 4.5 | 4 | 12 | 16.125
14 | 12 | 1 | 5 | 4.25 | 13.25 | 17.75
16 | 16 | 1 | 5.25 | 4.5 | 15.25 | 20.25
18 | 16 | 1.125 | 5.75 | 4.75 | 17.25 | 21.625
20 | 20 | 1.125 | 6 | 5.25 | 19.25 | 23.875
22 | 20 | 1.25 | 6.5 | 5.5 | 21.25 | 26
24 | 20 | 1.25 | 6.75 | 5.75 | 23.25 | 28.25
Series 300 Flange Raised Face
Nominal | Flange Bolts |  | Length |  | Gasket
Diameter | Qty | Size | Stud | Mach | ID | OD
0.5 | 4 | 0.5 | 2.5 | 2 | 0.625 | 2.125
0.75 | 4 | 0.625 | 2.75 | 2.5 | 0.8125 | 2.625
1 | 4 | 0.625 | 3 | 2.5 | 1 | 2.875
1.25 | 4 | 0.625 | 3 | 2.75 | 1.375 | 3.25
1.5 | 4 | 0.75 | 3.5 | 3 | 1.625 | 3.75
2 | 8 | 0.75 | 3.5 | 3 | 2 | 4.375
2.5 | 8 | 0.75 | 3.75 | 3.25 | 2.5 | 5.125
3 | 8 | 0.75 | 4 | 3.5 | 3 | 5.875
3.5 | 8 | 0.75 | 4.25 | 3.75 | 3.5 | 6.5
4 | 8 | 0.75 | 4.25 | 3.75 | 4 | 7.25
5 | 8 | 0.75 | 4.5 | 4 | 5 | 8.5
6 | 12 | 0.75 | 4.75 | 4.25 | 6 | 9.875
8 | 12 | 0.875 | 5.25 | 4.75 | 8 | 12.125
10 | 16 | 1 | 6 | 5.25 | 10 | 14.25
12 | 16 | 1.125 | 6.5 | 5.75 | 12 | 16.625
14 | 20 | 1.125 | 6.75 | 6 | 13.25 | 19.125
16 | 20 | 1.25 | 7.25 | 6.5 | 15.25 | 21.25
18 | 24 | 1.25 | 7.5 | 6.75 | 17 | 23.5
20 | 24 | 1.25 | 8 | 7 | 19 | 25.75
22 | 24 | 1.5 | 8.75 | 7.5 | 21 | 27.75
24 | 24 | 1.5 | 9 | 7.75 | 23 | 30.5